Myerstown, PA  17067

September 11, 2025

Chairman Patrick Angley called the regular monthly meeting to order at 7:00 p.m., prevailing time.  The meeting was held in the Conference Room of the Myerstown Water Treatment Facility situated at 601 Stracks Dam Road, Myerstown, PA, 17067.

ROLL CALL:

Present were: Steven Hammer; Treasurer Bryan Rittle; Secretary Brian Ziegler; Vice Chairman Samuel Moyer: Chairman Patrick Angley; Engineer Farley F. Fry; Solicitor Kenneth Sandoe; and Business Manager Steven Hickernell and Operations Manager Casey Walborn.

MINUTES:

Motion by Mr. Hammer; Second by Mr. Rittle:  To approve the minutes of the August 14, 2025 meeting as distributed.  Motion passed unanimously.

CITIZEN’S COMMENTS

Bruce Stegman from Kleinfelder Engineering gave a presentation and answered questions on pressure grouting of the Water Plant foundation to stabilize the walls of the building.

COMMUNICATIONS:

- PMAA Authorities on the Air letter

- McKenna Thank you letter

- Comm. Of PA. Share Account Program guidelines booklet

- 461 W. Main Ave. preliminary apartment complex inquiry call

INVOICES:

Motion by Mr. Ziegler; Second by Mr. Rittle:  To approve payment of the invoices as presented and attached.  Motion passed unanimously.

.

FINANCIAL REPORT:

Was reviewed.

OPERATIONS REPORT FOR SEPTEMBER 2025:

- Received a phone call from 188 N. Ramona Rd. He wasn’t happy with the how bumpy the area is where our watermain was laid. I consulted with Farley Fry and decided the project was long over and grass had been established since early May. There were A LOT of concessions made for the landowner throughout the project. I told him we were not going to do anything further

- Flushing of dead end hydrants and blow offs has been completed

- Paving of S. Railroad from Center ave. to Richland ave. has been completed. A few of our valve boxes were damaged by the paving company. They fixed all of them. I found one valve to be paved over. Dave Fake was notified and he is having the paving take care of it

- Tank Inspection report was received from Southern Corrosion Control. The Ground Tank is complete satisfactory. The Elevated Tank was graded satisfactory but Interior was “Moderate - The type of deficiencies noted are in the beginning stages of affecting the integrity of the coating system and Proportional - Deficiencies are proportional to the age of the coating and the impact of the environment.” It will need to be re-painted in the next few short years. I can provide full reports if you’d like

- Duffey will begin another round of meter replacements in October

- Ditchcreek completed televising the floor drain piping from the plant to the chemical holding manholes. Full video is available

- Void under the floor – with the pipe having a separation (photo available) I believe it will need slip lined. The size of the vertical pipe might make that a problem. I’m waiting for a call back from some slip lining companies with details on what is possible

- Gun-Krete - void under the floor in the chemical room. Met with them on Aug. 4th. Received a quote and is available for review

- Received a fine from the PUC from when AH Moyer hit a communications line on McKinley Ave. Apparently as the “Project Owner” I was supposed to submit an “Alleged Violation Report” within 30 days of a line strike or other violation. Also, it is required by the PUC that I do an “Online Compliance Training”

- Additional service line was installed at 812 S. Railroad by A.H. Moyer. 1” municipex

- Lead and Copper letters were sent out to the 20+ sample sites approved by DEP. Awaiting return letter. Will be putting sample bottles out for those sites on 9/16 and collecting the following day for our tri-annual required testing.

- Water Service Professionals completed a filter inspection on #1. We will have one more inspection this year for the 4th quarter

- Filter #2 is giving problems with the level floats. Will be replacing them ASAP

- Well #6 – spoke with the electrician today. He is still working on getting all of the parts to fix everything. Complete new wire will not need to be run. It is split inside and he can just replace that particular section

| Date |  | Well #3 |  | Well #5 |  | Well #6 |  | Well #8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 8/14/2025 |  | 21' P |  | 25' P |  | 18' P |  | N/A |
| 8/21/2025 |  | 20' P |  | 19' S |  | 17' S |  | N/A |
| 8/28/2025 |  | 22' P |  | 30'P |  | 20'P |  | N/A |
| 9/11/2025 |  | 28' P |  | 29' S |  | 25' S |  | N/A |

OFFICE REPORT SEPTEMBER 2025

- There were 0 new connection fees paid since last meeting.

- There was 1 bad debit last month. It paid immediately, realizing it was taken out of an old account so we did not charge a fee.  Also, 39 Wheatland finally paid their bad debit.

- Shutoff notices were sent to 55 properties this month.

- We posted 21 properties this month.  Dale Shiffer, of 300 E. Carpenter Ave. threatened Ryan Ward not to post his property.  I notified the Borough Code Enforcement Officer.

- 556 W. Main Ave. was shut off and called to pay.  He is on the road a lot so I showed him the way to pay online and he will in the future.

- We met by phone with Invoice Cloud and resolved most issues we had.

- My new computer was installed yesterday and is working.  My printer has finally broken down completely and will need to be replaced.

- Attached is a copy of the most recent Auditor’s Report that I do monthly.

CASH POSITION:

Was reviewed.

SOLICITOR’S REPORT:

The Solicitor reported that all of the easements are completed.

ENGINEER’S REPORT:

Was reviewed.

Motion by Mr. Rittle; Second by Mr. Moyer: To have the Engineer draft a change order to repair the problematic water main on W. Richland Ave.  Motion passed unanimously.

OLD BUSINESS:

The Transmission Main update was discussed in the Engineer’s Report.

The Railroad St. Project was discussed in the Engineer’s Report.

The termination and release of easements pertaining to the Transmission Main Project were discussed in the Solicitor’s Report.

NEW BUSINESS:

The following motions were all made as one by Mr. Hammer; Second by Mr. Moyler:

Invoice #s 200187 for $369.45

200192 for $909.88

200188 for $1080.50

200190 for $4708.26

All to Hanover Engineering from the General Fund.  Motion passed unanimously.

Motion by Mr. Rittle; Second by Mr. Ziegler: To approve Invoice # 200189 for $516.63 to Hanover Engineering from the 651 W. Lincoln Ave. Escrow Account.  Motion passed unanimously.

The following motions were all made as one by Mr. Moyer; Second by Mr. Rittle:

Invoice #s 200186 for $13042.58 to Hanover Engineering

200191 for $3860.05 to Hanover Engineering

18048 for $943.00 to Steiner & Sandoe Attorneys at Law

From the Wilmington Trust Account.  Motion passed unanimously.

Motion by Mr. Rittle; Second by Mr. Hammer: To approve the 2026 Minimum Municipal Obligation for PMRS with an estimate of $18,100.00.  Motion passed unanimously.

No action was taken on the Keystone Gun-Krete quote for the Chemical Room floor.

Motion by Mr. Hammer; Second by Mr. Ziegler: To approve the installation of 400 meters in the Wheatland Manor area by Mr. Todd Duffey at a cost of $76.00 per meter. (Mr. Duffey is now a Co-Stars certified vendor).  Motion passed unanimously.

Motion by Mr. Rittle; Second by Mr. Hammer: To Have Garcia, Garman and Shea PC audit the 2025 year of business.  Motion passed unanimously.

Motion by Mr. Angley; Second by Mr. Rittle: To Approve an additional water unit for 621 S. Railroad St.  Motion passed unanimously.

ADJOURNMENT:

No further business to come before the meeting, the meeting was adjourned at 9:25 P.M., prevailing time.

Respectfully submitted,

Brian Ziegler

Secretary

Transcribed by Terry Miller

Asst. Sec.

`